Form 72—fire hydrant and sprinkler system periodic testing and maintenance

Version 1 – July 2014

This form is to be used for the purposes of maintenance to water based fire safety installations, as required by the Queensland Development Code – Mandatory Part (MP) 6.1, which is a building assessment provision under the Building Act 1975, section 30. This form is also to be used in accordance with the ‘Fire hydrant and sprinkler system commissioning and periodic maintenance procedure’, defined in MP 6.1 as the ‘Relevant procedure’. Please note that this form does not comprise all maintenance requirements—this form is only for collecting results for maintenance for some sections of the Australian Standards referred to and in each case, further testing is required.

| Part A—Test details |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Site name |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Site address |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Contractor |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test details | Test date: |  |  |  |  |  |  |  |  |  |  |  |  |  | Maintenance test: Annual 5 year fire hydrant fire sprinkler combined |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Time: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part B—Hydrant hydrostatic test |  |  |  |  |  |  |  |  |  |  |  | PASS |  |  |  |  |  |  |  |  |  | FAIL |  |  |  |  |  |
| Refer to the required pressure specification for periodic testing (as applicable) as per AS2419.1 or AS1851. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Boost pressure |  | kPa |  |  |  |  |  | Test pressure |  |  |  |  |  |  |  | kPa |  |  |  |  |  |  |  |  |  |  |  |
| Duration of test |  | mins |  |  |  |  |  | End of test pressure |  |  |  |  |  |  |  | kPa |  |  |  | Loss (if any): |  |  |  |  |  | L/min |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part C—Hydrant test equipment/pressure gauges |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| If using more devices, provide details in the Notes section below or complete another form. The correction factor must be kPa or a percentage. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Flow measuring device |  |  |  | Orifice |  |  |  |  |  |  |  |  |  | Mechanical |  |  |  |  |  |  |  |  |  | Electro magnetic |  |  |  |
|  |  |  |  | Part C not required for orifice testing |  |  |  |  |  |  |  |  |  | Calibrated: / / |  |  |  |  |  |  |  |  |  | Calibrated: / / |  |  |  |
|  |  |  |  | Device/gauge 1 |  |  |  |  | Device/gauge 2 |  |  |  |  |  |  |  |  | Device/gauge 3 |  |  |  |  |  |  | Device/gauge 4 |  |  |
| Serial number |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date calibrated |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Correction certificate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 65/100/150 mm face |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Digital reader |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Increments (kPa) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part D—Hydrant system flow test |  |  |  |  |  |  |  |  |  |  |  |  | PASS |  |  |  |  |  |  |  |  |  | FAIL |  |  |  |  |
| This part relates to tests under Section 4 of AS1851. If pressure/flow rates do not meet the fire system design criteria and there are no on-site problems, contact the relevant water service provider to ascertain if there are any problems with the water system network. In the table below, please record the pressure readings obtained during the hydrant system flow test. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrant 1 location |  |  |  |  |  |  |  |  |  |  | Hydrant 3 location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrant 2 location |  |  |  |  |  |  |  |  |  |  | Hydrant 4 location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| System requirements |  |  | L/s at |  |  |  | kPa |  |  |  | Static pressure |  |  |  |  |  |  |  | kPa |  |  |  |  |  |  |  |  |
| On-site pump set installed |  |  |  |  |  | Yes |  |  |  |  |  |  |  |  |  |  |  |  | No |  |  |  |  |  |  |  |  |
| Pressure zone number: |  |  | Size/flow rate |  | Device/gauge no. (Part C) |  |  |  |  | Hydrant 1 only |  |  |  |  |  |  | Hydrants 1 and 2 |  |  |  | Hydrants 1, 2 and 3 |  |  |  |  |  | Hydrants 1, 2, 3 and 4 |
| Nozzles |  |  | 19 mm |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
|  |  |  | 22 mm |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
|  |  |  | 25 mm |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
| Other portable testing devices |  |  | 5 L/s |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
|  |  |  | 10 L/s |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
|  |  |  | 15 L/s |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
|  |  |  | 20 L/s |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
|  |  |  | 30 L/s |  |  |  |  |  |  | kPa |  |  |  |  |  |  | kPa |  |  |  | kPa |  |  |  |  |  | kPa |
|  |  |  | System achieved: L/s at kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Part E—Pump appliance booster test |  |  |  |  |  |  |  |  |  | PASS |  |  |  | FAIL |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| This part relates to sections 10.4 and 10.5 of AS2419.1 and for tests under Section 4 of AS1851. If pressure/flow rates do not meet the fire system design criteria and there are no on-site problems, contact the relevant water service provider to ascertain if there are any problems with the water system network. In the table below, please record the pressure readings obtained during the pump appliance booster test. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydrant locations |  |  |  |  |  |  |  |  |  |  | Height of highest hydrant above booster |  |  |  |  |  | m |
| System requirements |  |  | L/s at kPa |  |  |  | Static pressure |  |  |  |  |  | kPa |  |  |  |  |
| Pump inlet pressure |  |  | kPa |  |  |  | Pump discharge pressure |  |  |  |  |  | kPa |  |  |  |  |
| Boost pressure |  |  | kPa |  |  |  | Calculated frictional loss |  |  |  |  |  | kPa |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part F—Sprinkler hydrostatic test |  |  |  |  |  |  |  |  |  | PASS |  |  |  | FAIL |  |  |  |
| Relevant required pressure specification in AS2118.1, AS2118.4 and AS2118.6. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Pressure |  |  | kPa |  |  |  |  | Time held |  |  |  |  |  | mins |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part G—Sprinkler system flow test |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| This section is to be used for sections 4.14 of AS2118.1-1999, 4 of AS2118.6-2012 and 6.2 of AS2118.4-2012 and section 2 of AS1851. Notes: (1) For AS2118.1 and AS2118.6 systems, multiple testing points may be required. (2) For AS2118.4, a simulated running test may be required for systems without a flow measuring device, in which the test involves opening a valve to discharge a volume of water that is accepted as being in excess of the design flow. System test points shall be noted for each different system and its location and descriptor. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | System specifications (block plan): |  |  |  |  |  |  |  |  |  |  | Test results: |  |  |  |  |  |
| Test point 1 | Location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Required flow rate |  |  |  |  | L/min |  |  |  |  |  | Pass Fail |  |  |  | L/min |  |
|  | Required pressure |  |  |  |  | kPa |  |  |  |  |  | Pass Fail |  |  |  | kPa |  |
| Test point 2 | Location |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Required flow rate |  |  |  |  | L/min |  |  |  |  |  | Pass Fail |  |  |  | L/min |  |
|  | Required pressure |  |  |  |  | kPa |  |  |  |  |  | Pass Fail |  |  |  | kPa |  |
| Running test | Installation gauge pressure: kPa |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part H—Compliance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Critical defects identified |  | Yes |  |  | Give owner/occupier a critical defect notice |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | No |  |  | No action required in relation to critical defects at this time |  |  |  |  |  |  |  |  |  |  |  |  |
| Repairs/corrective actions taken |  | Yes |  |  | Attach details (including action and date taken) as part of Licensee’s report |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | No |  |  | No action required in relation to repairs/corrective actions at this time |  |  |  |  |  |  |  |  |  |  |  |  |
| System |  | Pass |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Fail |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Part I—Signature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| By signing this Form 72, I confirm that the information contained herein is correct to the best of my knowledge given the information available and that this Form 72 has been completed in accordance with the relevant standards, codes and regulations. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Licensee name |  |  |  |  |  |  |  |  | Licensee signature |  |  |  |  |  |  |  |  |
| Licence no. (QBCC/PIC) |  |  |  |  |  |  |  |  | Licensee report no. |  |  |  |  |  |  |  |  |

Note: Building owners/occupiers are responsible for ensuring their buildings continuously meet fire safety standards. Where a building owner/occupier becomes aware that their building does not meet the minimum requirements for water pressure required by any standard applicable under the Queensland Development Code Mandatory Part 6.1 (Maintenance of fire safety installations) the building owner/occupier should contact the Queensland Fire and Emergency Service.

Definitions  “Maintenance test” means a test that is required under a maintenance standard such as AS1851. “Running test” means a two inch waste test installed at the sprinkler control valve on older systems.

Privacy:  The information on this form is collected for purposes related to monitoring compliance under the Plumbing and Drainage Act 2002, the Building Act 1975 and the Building Fire Safety Regulation 2008 (“legislation”). This information may be stored in the department’s database and may be used for statistical research, information provision and evaluation of Plumbing Industry Council and state government services. Your personal information may be disclosed to other government agencies, local government authorities and third parties for purposes related to this application. Except for these circumstances, personal information will only be disclosed to third parties with your consent or in accordance with the Information Privacy Act 2009.

RTI: The information collected on this form will be retained as required by the Public Records Act 2002 and other relevant Acts and regulations, and is subject to the Right to Information regime established by the Right to Information Act 2009. If you have any further questions regarding your privacy, please email Building Codes Queensland on buildingcodes@qld.gov.au. © The State of Queensland (Department of Housing and Public Works) 2014. Published by the Queensland Government July 2014, 41 George Street, Brisbane QLD 4000.